## 5_10_15
Engineering & Physical Data
MODEL |  | OUTDOOR UNIT |  |  |  | ATYN20LV1 | ATYN25LV1 | FTYN25LV1 | ATYN35LV1 | FTYN35LV1 | ATYN50LV1 | FTYN50LV1 | ATYN60LV1 | FTYN60LV1
|  | TYPE |  |  |  | ARYN20LV1 | ARYN25LV1 | RYN25LV1 | ARYN35LV1 | RYN35LV1 | ARYN50LV1 | RYN50LV1 | ARYN60LV1 | RYN60LV1
NOMINAL COOLING CAPACITY |  |  |  |  | Btu/h | 7300 | 9040 | 9040 | 11300 | 11300 | 17900 | 17900 | 20500 | 20500
[5 empty] | W | 2140 | 2650 | 2650 | 3300 | 3300 | 5250 | 5250 | 6010 | 6010
NOMINAL HEATING CAPACITY |  |  |  |  | Btu/h | 7000 | 9550 | 9550 | 11800 | 11800 | 18900 | 18900 | 21700 | 21700
[5 empty] | W | 2060 | 2800 | 2800 | 3470 | 3470 | 5550 | 5550 | 6350 | 6350
NOMINAL TOTAL INPUT POWER (COOLING) |  |  |  |  | W | 650 | 825 | 825 | 1080 | 1080 | 1635 | 1635 | 1870 | 1870
NOMINAL TOTAL INPUT POWER (HEATING) |  |  |  |  | W | 560 | 775 | 775 | 980 | 980 | 1480 | 1480 | 1740 | 1740
NOMINAL RUNNING CURRENT (COOLING) |  |  |  |  | A | 2.91 | 3.7 |  | 4.99 |  | 7.19 |  | 8.26
NOMINAL RUNNING CURRENT (HEATING) |  |  |  |  | A |  | 3.47 |  | 4.55 |  | 6.49 |  | 7.68
EER |  |  |  |  | W/W | 3.29 | 3.21 | 3.21 | 3.06 | 3.06 | 3.21 | 3.21 | 3.21 | 3.21
COP |  |  |  |  | W/W | 3.68 | 3.61 | 3.61 | 3.54 | 3.54 | 3.75 | 3.75 | 3.65 | 3.65
REFRIGERANT CHARGE |  |  |  |  | kg | 0.65 | 0.8 | 0.8 | 0.85 | 0.85 | 1.45 | 1.45 | 1.65 | 1.65
POWER SOURCE |  |  |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
REFRIGERANT TYPE | [5 empty] | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A
INDOOR UNIT | CONTROL | AIR DISCHARGE |  |  |  | NON DUCTED | NON DUCTED |  | NON DUCTED |  | NON DUCTED |  | NON DUCTED
|  | OPERATION |  |  |  | LCD REMOTE CONTROL | LCD REMOTE CONTROL |  | LCD REMOTE CONTROL |  | LCD REMOTE CONTROL |  | LCD REMOTE CONTROL
| AIR FLOW | TURBO |  |  | l/s / CFM | 130/275 | 169/ 358 | 169/ 358 | 176/ 372 | 176/ 372 | 280/ 594 | 280/ 594 | 303 / 641 | 303 / 641
|  | HIGH |  |  | l/s / CFM | 124/262 | 161/ 342 | 161/ 342 | 168/ 355 | 168/ 355 | 251/ 531 | 251/ 531 | 290/ 614 | 290/ 614
|  | MEDIUM |  |  | l/s / CFM | 107/227 | 133/ 282 | 133/ 282 | 141/ 298 | 141/ 298 | 224/ 474 | 224/ 474 | 253/ 537 | 253/ 537
|  | LOW |  |  | l/s / CFM | 92/195 | 106/ 225 | 106/ 225 | 114/ 242 | 114/ 242 | 199/ 422 | 199/ 422 | 224/ 474 | 224/ 474
|  | QUIET |  |  | l/s / CFM | 86/182 | 99/ 209 | 99/ 209 | 106/ 225 | 106/ 225 | 180/ 381 | 180/ 381 | 197/ 418 | 197/ 418
| SOUND PRESSURE LEVEL (T/H/M/L/Q) |  |  |  | dBA | 37/36/31/25/24 | 39/ 37/ 33/ 27/ 25 | 39/ 38/ 33/ 27/ 25 | 40/ 39/ 35/ 29/ 28 | 41/ 40/ 35/ 29/ 27 | 44/ 42/ 39/ 36/ 35 | 44/ 42/ 39/ 36/ 34 | 48/ 46/ 43/ 39/ 37 | 48/ 46/ 43/ 40/ 37
| UNIT DIMENSION |  | HEIGHT X WIDTH X DEPTH |  | mm | 288 X 800 X 206 | 288 X 800 X 206 | 288 X 800 X 206 | 288 X 800 X 206 | 288 X 800 X 206 | 310 x 1065 x 224 | 310 x 1065 x 224 | 310 x 1065 x 224 | 310 x 1065 x 224
| PACKING DIMENSION |  | HEIGHT X WIDTH X DEPTH |  | mm | 344 X 874 X 274 | 344 X 874 X 274 | 344 X 874 X 274 | 344 X 874 X 274 | 344 X 874 X 274 | 370 x 1121 x 285 | 370 x 1121 x 285 | 370 x 1121x 285 | 370 x 1121x 285
| UNIT WEIGHT |  |  |  | kg | 9 | 9 |  | 9 |  | 14 |  | 14
| CONDENSATE DRAIN SIZE |  |  |  | mm | 19 | 19 |  | 19 |  | 19.05 |  | 19.05
| FAN | TYPE |  |  |  | CROSS FLOW | CROSS FLOW |  | CROSS FLOW |  | CROSS FLOW |  | CROSS FLOW
|  | DRIVE |  |  |  | DIRECT | DIRECT |  | DIRECT |  | DIRECT |  | DIRECT
| FAN MOTOR | TYPE |  |  |  | 1-PHASE SCR | 1-PHASE SCR |  | 1-PHASE SCR |  | 1-PHASE SCR |  | 1-PHASE SCR
|  | INDEX OF PROTECTION (IP) |  |  |  | IP20 | IP20 |  | IP20 |  | IP 44 |  | IP44
|  | INSULATION GRADE |  |  |  | CLASS E | CLASS E |  | CLASS E |  | CLASS E |  | CLASS E
|  | RATED INPUT POWER |  |  | W | 26 | 32 |  | 40 |  | 57 |  | 72
|  | RATED RUNNING CURRENT |  |  | A | 0.19 | 0.17 |  | 0.2 |  | 0.27 |  | 0.34
|  | MOTOR OUTPUT |  |  | W | 18 | 18 | 18 | 18 | 18 | 26 | 26 | 30 | 30
|  | POLES |  |  |  | 4 | 4 |  | 4 |  | 4 |  | 4
| COIL | TUBE | MATERIAL |  |  | SEAMLESS INNER GROOVE COPPER | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER
|  |  | DIAMETER |  | mm | 7 | 7 |  | 7 |  | 7 |  | 7
|  | FIN | MATERIAL |  |  | ALUMINIUM (HYDROPHILIC FIN) | ALUMINIUM (HYDROPHILIC FIN) |  | ALUMINIUM (HYDROPHILIC FIN) |  | ALUMINIUM (HYDROPHILIC FIN) |  | ALUMINIUM (HYDROPHILIC FIN)
|  |  | FACE AREA |  | m2 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.29 | 0.29 | 0.29 | 0.29
|  |  | ROW |  |  | 2 | 2 |  | 2 |  | 2 |  | 2
| AIR QUALITY | FILTER | TYPE |  |  | SARANET | SARANET | SARANET | SARANET | SARANET | SARANET | SARANET | SARANET | SARANET
|  |  | QUANTITY |  | pc | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| CASING |  |  |  | COLOUR | WHITE | WHITE |  | WHITE |  | WHITE |  | White
OUTDOOR UNIT | AIR FLOW |  |  |  | l/s / CFM | 297/630 | 396/ 840 | 396 | 457/ 969 | 457 | 618/ 1310 | 618 | 684/ 1450 | 684
| SOUND PRESSURE LEVEL |  |  |  | dBA | 44 | 46 | 46 | 49 | 49 | 52 | 52 | 52 | 52
| UNIT DIMENSION |  | HEIGHT X WIDTH X DEPTH |  | mm | 494 X 600 X 245 | 540 X 700 X 250 | 540 X 700 X 250 | 540 X 700 X 250 | 540 X 700 X 250 | 651 x 855 x 328 | 651 x 855 x 328 | 753 x 855 x 328 | 753 x 855 x 328
| PACKING DIMENSION |  | HEIGHT X WIDTH X DEPTH |  | mm | 535 X 721 X 331 | 596 X 803 X 323 | 596 X 803 X 323 | 596 X 803 X 323 | 596 X 803 X 323 | 693 x 990 x 415 | 693 x 990 x 415 | 793 x 990 x 415 | 793 x 990 x 415
| UNIT WEIGHT |  |  |  | kg | 24 | 29 |  | 31 |  | 49 |  | 50
| PIPE CONNECTION | TYPE |  |  |  | FLARE VALVE | FLARE VALVE |  | FLARE VALVE |  | FLARE VALVE |  | FLARE VALVE
|  | SIZE | LIQUID |  | mm | 6.35 | 6.35 |  | 6.35 |  | 6.35 |  | 6.35
|  |  | GAS |  | mm | 9.52 | 9.52 |  | 12.7 |  | 12.7 |  | 15.88
| FAN | TYPE |  |  |  | PROPELLER | PROPELLER |  | PROPELLER |  | PROPELLER |  | PROPELLER
|  | DRIVE |  |  |  | DIRECT | DIRECT |  | DIRECT |  | DIRECT |  | DIRECT
| FAN MOTOR | TYPE |  |  |  | INDUCTION | INDUCTION |  | INDUCTION |  | INDUCTION |  | INDUCTION
|  | INDEX OF PROTECTION (IP) |  |  |  | IP23 | IP23 |  | IP44 |  | IP 44 |  | IP23
|  | INSULATION GRADE |  |  |  | CLASS B | CLASS B |  | CLASS B |  | CLASS B |  | CLASS F
|  | RATED INPUT POWER |  |  | W | 37 | 52 |  | 59 |  | 105 |  | 123
|  | RATED RUNNING CURRENT |  |  | A | 0.16 | 0.23 |  | 0.26 |  | 0.46 |  | 0.54
|  | MOTOR OUTPUT |  |  | W | 20 | 21 | 21 | 30 | 30 | 43 | 43 | 60 | 60
|  | POLES |  |  |  | 6 | 6 |  | 6 |  | 8 |  | 6
| COMPRESSOR | TYPE |  |  |  | RB68A/ RREOL ALPHA68M | ROTARY |  | ROTARY |  | ROTARY |  | ROTARY
|  | OIL TYPE |  |  |  | 300 | FV50S |  | FV50S |  | FV50S |  | FV50S
|  | OIL AMOUNT |  |  | cm3 | 642 | 350 |  | 350 |  | 670 |  | 670
|  | RATED INPUT POWER (COOLING) |  |  | W | 495 | 736 | 736 | 981 | 981 | 1473 | 1473 | 1675 | 1675
|  | RATED INPUT POWER (HEATING) |  |  | W | 2.81 | 686 | 686 | 879 | 879 | 1318 | 1318 | 1545 | 1545
|  | RATED RUNNING CURRENT (COOLING) |  |  | A | 2.81 | 3.28 | 3.28 | 4.53 | 4.53 | 6.46 | 6.46 | 7.38 | 7.38
|  | RATED RUNNING CURRENT (HEATING) |  |  | A | 2.19 | 3.05 | 3.05 | 4.08 | 4.08 | 5.76 | 5.76 | 6.8 | 6.8
|  | LOCKED ROTOR AMP. |  |  | A | 12.4 | 15.8 | 15.8 | 23 | 23 | 32 | 32 | 32.3 | 32.3
| COIL | TUBE | MATERIAL |  |  | SEAMLESS INNER GROOVE COPPER | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER |  | SEAMLESS INNER GROOVE COPPER
|  |  | DIAMETER |  | mm | 7 | 7 |  | 9.52 |  | 7 |  | 7
|  | FIN | MATERIAL |  |  | ALUMINIUM (RAISE LANCE) | ALUMINIUM (RAISE LANCE) |  | ALUMINIUM (SLIT) |  | ALUMINIUM (RAISE LANCE) |  | ALUMINIUM (CORRUGATED)
|  |  | FACE AREA |  | m2 | 0.29 | 0.35 |  | 0.36 |  | 0.5 |  | 0.61
|  |  | ROW |  |  | 1 | 1 |  | 1 |  | 2 |  | 2
| CASING |  |  |  | COLOUR | Ivory White | Ivory White |  | Ivory White |  | Ivory White |  | Ivory White
1) ALL UNITS ARE BEING TESTED AND COMPLY TO ISO 5151 (NON-DUCTED UNIT) OR ISO 13253 (DUCTED UNIT).
2) ALL SPECIFICATIONS ARE SUBJECTED TO CHANGE BY THE MANUFACTURER WITHOUT PRIOR NOTICE.
|  |  |  | COOLING |  |  | HEATING
|  |  |  | INDOOR: 27°C DB / 19°C WB |  |  | INDOOR: 20°C DB
|  |  |  | OUTDOOR: 35°C DB / 24°C WB |  |  | OUTDOOR: 7°C DB / 6°C DB